AIR CONDITIONING

OBJECTIVE  :- Upon completion of this unit you should be able to

- Know about the air conditioning and details of RDSO specification 4 A.C -1-70

- Understand the refrigeration cycle and air cycle

- Know about refrigerant

- Know about the important components

- Understand the electrical system for S.G and EOG Coaches

Structure:-

  - Introduction

  - Details of RDSO specification

  - Refrigeration cycle

  - Air cycle

  - Refrigerant

  - Important components

  - Electrical power supply system

  - Maintenance Works

  - Summary

  - Self assessment exercises

  - Introduction :--With the improvement in standard of living in India, the average passenger requires comfortable travel. Air-conditioned coaches in Indian Railway provide comfortable travel to the passengers particularly those moving over long distance across our country.

In air conditioning process a constant climatic condition is maintained by controlling --Temperature, Humidity, Cleanliness, Noise and Air motion. This includes both refrigeration and heating depending upon ambient temperature.

Refrigeration is the process of lowering the temp. of an object below that of its surroundings.

  - RDSO Specification No 4 AC-1-7 0: --It specifies the capacity of A C plant will be sufficient to maintain the internal temp. at 23 to 25 degree centigrade and relative humidity 40 to 60 % ( DB ) and 25 to 28 % (WB) with full compartment to passengers,lights,fans e.t.c It also specifies that the equipments should be admit fresh air of 0.3 meter cube per passenger

  - Refrigeration Cycle: --The refrigerant gas at low pressure is compressed by compressor. This compression raises the pressure up to 150-psi (180-psi maximum) and the gas temp rises to super heat condition. As the gas passes through the condenser, the super heat and latent heat is removed at constant pressure. At the expansion value, the expansion takes place giving the refrigeration effect in the evaporator.

  - Air Cycle: --The movement of air inside coach is created by centrifugal pump in the evaporator unit. Out side air is admitted through fresh air filters mounted on the sidewall of the coach. Fresh air is mixed with a portion of the return air through return air filters. This mixture is drawn over the evaporator and then delivered into the air duct through which it is distributed in the coaches. The air inside the coach absorbing heats and returns to the blower thus completing the cycle.

1.5 Refrigerant: --The gas used in AC system is known as refrigerant. It should have the following properties-

- It should be incorrosive.

- It should not have a disagreeable odour.

- Latent heat of vaporization should be large.

- Volume of vapour for a given weight should be low.

- The pressure required for condensing at operating temp. should be low.

FREON 12(CCl2F2)[Diflouro Dichloro Methane]—It has excellent refrigeration property and is safe, non-toxic, non-flammable, non-corrosive and leakage are easily detectable.

R-22 [Di-ChloroFloro Methane](CHCl2F2) -- Now it is used as Refrigerant as it requires in small amount compare to Freon 12.

  - Main components of an AC system: --The following are the main components-

- Compressor—It is multicylinder, reciprocating type. It compresses the refrigerant vapour up to maximum 180-psi. This compression raises the temp. at the boiling of the refrigerant.

- Condenser—It extracts the heat absorbing by the refrigerant vapour during compression .It consists of heat exchanger which is forced cooled by two or three axial flow blower fans. The refrigerant vapour is cooled at constant pressure and at constant pressure and liquefied

- Expansion Valve—The main function of an expansion valve is to control the quantity of the liquid refrigerant admitted into the cooling coils of the evaporator The heat load of evaporator constantly varies accordingly upon heat gain within air conditioned space.

- Evaporator Unit---It consists of thermostatic expansion valve, a heat exchanger resistance heating unit and a centrifugal blower driven by motor. The cooled air lead through ducting to the various compartments. When the ambient temp. is very low refrigeration is not required,the heater is switched on automatically according to thermostat setting.

  - Electrical power supply system: -

- For SG Coach—The power supply is received from two nos. Brushless Alternator 18Kw each, with static rectifier and regulator unit. The Alternators (one in one bogie) are suspended from a bracket welded on the bogie transom and driven by coach axle by a set of V belts of section C.DC output from the two Alternators are parallel with the battery. The input of the Alternator is 415 Volts, 3 phase, AC and the output voltage is 104 to 140 volts DC with tap changer.

- For EOG Coach—The power supply for AC equipments, lights and fans is drawn from one of the two feeders of 415 volts 3 phase 50 Hz emanating from power car attached one either end of the train. The compressor motor, condenser blower and heaters in the evaporator operate at 415V 3-phase 50 Hz and evaporator blower operates at110V 3-phase AC obtained from control transformer 415/110-Volt 3-phase, 2.5 KVA capacity.

  - Maintenance:--The following maintenance s are required for AC system—

- Compressor, condenser, evaporator Motor—Checking of coupling condition and attention, carry out visual inspection for any signs of heating and fumes. Blowing of dust. Check rotation of motor for correctness. Cleaning and tightening of electrical connections.

- Compressor-Level of oil, checking of readings of HP, LP and OP gauge.

- Condenser—Cleaning of fins with high pressure jet.Check the connection for any abnormality

- Filters—Cleaning/Replacing filters unit. Checking of fresh air dampers for working order.

- Thermostat—Checking for any abnormality.

- Panel boards—Cleaning by vacuum cleaner and checking of indicating pilot lamps and contactors for their working order.

- Cables—Check the earth leakage in the wiring.

1.9 Summary—Removal of heat from enclosures with a purpose to cool them is known as refrigeration. In almost all refrigerators cooling is achieved by the evaporation of a liquid known as refrigerant. During its transformation from the liquid to the vapor state the refrigerant absorbs latent heat of evaporation which is supplied partially by the liquid itself and partially by the surrounding medium resulting fall in temp.

In an AC process a constant climatic condition is maintained by controlling the temp.humidity, cleanness, noise, and air motion. This includes both the refrigeration and heating depending upon the ambient temp. The main components of an AC are compressor, condenser expansion and evaporator unit. The electrical supply system is obtained from SOG and EOG system.

  - Self assessment exercises:-

- What do you mean by ref rigeration and air conditioning?

- Explain refrigeration and air cycle?

- What are the main components and their functions of an AC system?

- What maintenances are required for an AC system?